## Slide 1: Hands-on Session Outline - PSCAD
Detailed walkthrough of the aggregate solar plant model
  where to find all the parameters
  what each subsystem does, etc.
[AT to explain how demos and breakout sessions will work]
Demo 1:
  Flat run at different power flow
  Repeat one at a smaller time step. Compare results.
Notes: Walk through:
Start at Main level – go over components of aggregate plant model
Show parameters of PPC. Then go inside PPC and show high level blocks
Back up and show parameters of solar farm module before going inside.
how P/Q cmd comes from PPC
how parameters are used inside the module
Electrical circuit
Control blocks – high level – emphasize PLL in Box 1
Demo 1 Instructor notes:
Is time step size acceptable per EMT model requirements (example, ERCOT, HECO, ISO-NE)?
Does it require specific time step size?
Try runing at odd time step, e.g. 7 microseconds

## Slide 2: Hands-on Session - PSCAD
Demo 2: Low voltage ride-through
  How to record COMTRADE data
  LLLG faults with different fault impedance
    0.5pu retained voltage for 0.3 sec – test PRC-24 level (<0.65pu for 0.3 sec)
    Try another
  LL, LG bolted fault
  Check relevant protection and trip settings
  Check reactive current injection settings
Demo 3: Pref step change
  Try commanding greater than limit
  Check P limits
Notes: Demo 2 Instructo notes:
Show Comtrade recorder settings and where the output is saved
There’s another UV trip level at <0.75pu for 2.0 sec.
Discuss how reactive current injection support voltage during faults and show where the settings are (there are under Solar Farm Parameters -> Aux. Control category)
Demo 3 Instructor notes:
Sum of all inverter capability can be more than site/plant operational limit for various reasons (oversized for capacity/production agreement, to cover losses etc.)
Pmax setting under Operational Limits under PPC is in pu based on 125 MVA = 50 (# of inverter) * 2.5 (MVA per inverter)
Pmax is initially set wrong to 1pu (125MW). So, it will produce more than 100MW shown as Plant Pmax in the example case

## Slide 3: Hands-on Session - PSCAD
Demo 4: Vref step change
  Verify Plant level reactive control mode
  Change Vref by +/- 2%
  Compare Q out at POC with Q limit
Demo 5: High voltage ride-through
  Why did it fail to ride through?
  Check relevant trip settings
Demo 6: Grid frequency change ride-through
  Check primary frequency response based on the droop setting and deadband
  Check relevant trip settings
Demo 7: Grid angle change ride-through (if time permits)
  : +/- 25 deg at different operating points
Notes: Demo 4 Instructor notes:
Grid is quite strong so even when Qcmd is at Qmax, it cannot move the POC voltage by 2%. (Optional: try increasing the grid impedance 2X and observe how much voltage moves)
PPC is limiting Q_cmd sent to inverter at Operational Q limit; it is not limiting Qout at POC to the Operational limit. This is obvious for -2% change where Q_POC is lower than 0.6pu Qmin.
  Discussion point: Is there a requirement to limit Qout at POC to certain level that is potentially lower than capability? Why even?
  Try running long than 10 secs to see how P is getting curtailed to pursue more Q until Q_cmd from PPC hits limit – is this acceptable? Question for TP/PC
  Is it model deficiency?
(FERC Order 827: dynamic reactive power within 0.95 leading to 0.95 lagging, only)
Demo 5 Instructor notes:
OV trip level set directly on PRC-24 curve. Due to initial power flow, inverter terminal voltage exceeds the PRC-24 level, causing a trip, although POC voltage is still below PRC-24 level.
Demo 6 Instructor notes:
Note that deadband setting in PPC total across the nominal (i.e. OF and UF deadbands are half of what’s entered for the setting (this is due to the way deadband component in Master library takes its parameter).
Deadband setting is 0.2Hz. So, delta_Freq = 61-60-0.2/2 = 0.9Hz or 0.015pu. Delta_P = 0.015/0.04 = 0.375pu
Try going to 57.8Hz. ERCOT PRC-24 level is <= 58Hz for 2 sec. Observe it doesn’t trip. Does it mean it passed? No, it didn’t trip because there is no OF/UF protection modeled. Lesson: without knowing what is and is not included in the model, the plant can’t be passed based on simulation test result alone.